{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":63,"n_cols":10,"rows_kept":63,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","BS-A14AV1B"]
[]
[]
[]
[]
["","","","","","BS4A14AJV1B","BS6A14AJV1B","BS8A14AJV1B","BS10A14AJV1B","BS12A14AJV1B"]
["Sound pressure level","Nom.","","","dBA","36.0 (1)","37.0 (1)","37.0 (1)","38.0 (1)","38.0 (1)"]
["Standard Accessories","Installation and operation manual","","","","1","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1","1"]
["","Drain hose","","","","1","1","1","1","1"]
["","Clamp for drain hose","","","","1","1","1","1","1"]
["","Sealing pad (small)","","","","1","1","1","1","1"]
["","Sealing pad (large)","","","","1","1","1","1","1"]
["","Sealing material","","","","1","1","1","1","1"]
["","Insulation tube for stopper pipes","","","","9","5","5","5","5"]
["","Tie-wraps","","","","8","11","11","11","11"]
["","Stopper pipes","","","","9","5","5","5","5"]
["","Accessory pipe","","","","14","14","14","14","14"]
["","Duct closing plate","","","","1","1","1","1","1"]
["Refrigerant","GWP","","","","675.0","675.0","675.0","675.0","675.0"]
["","Type","","","","R-32","R-32","R-32","R-32","R-32"]
["BS box system safety requirements","Duct connection diameter on unit","","","mm","160.0","160.0","160.0","160.0","160.0"]
["","Duct connection positions","","","","Left/Right","Left/Right","Left/Right","Left/Right","Left/Right"]
["Maximum number of connectable indoor units per branch","","","","","5","5","5","5","5"]
["Operation range","Temperature around casing","","Min.","°CDB","15","15","15","15","15"]
["","","","Max.","°CDB","32","32","32","32","32"]
["","Humidity around casing","","Max.","%","80","80","80","80","80"]
["Maximum number of connectable indoor units","","","","","20","30","40","50","60"]
["Piping connections","Outdoor unit or Refrigerant Flow Through","Discharge gas","Type","","Brazing connection","Brazing connection","Brazing connection","Brazing connection","Brazing connection"]
["","","","OD","mm","12.7 (3), 15.9 (3), 19.1 (3), 22.2","12.7 (3), 15.9 (3), 19.1 (3), 22.2","12.7 (3), 15.9 (3), 19.1 (3), 22.2","12.7 (3), 15.9 (3), 19.1 (3), 22.2","12.7 (3), 15.9 (3), 19.1 (3), 22.2"]
["","","Liquid","Type","","Brazing connection","Brazing connection","Brazing connection","Brazing connection","Brazing connection"]
["","","","OD","mm","9.5 (3), 12.7 (3), 15.9","9.5 (3), 12.7 (3), 15.9","9.5 (3), 12.7 (3), 15.9","9.5 (3), 12.7 (3), 15.9","9.5 (3), 12.7 (3), 15.9"]
["","","Gas","OD","mm","15.9 (3), 19.1 (3), 22.2, 28.6 (3)","15.9 (3), 19.1 (3), 22.2, 28.6 (3)","15.9 (3), 19.1 (3), 22.2, 28.6 (3)","15.9 (3), 19.1 (3), 22.2, 28.6 (3)","15.9 (3), 19.1 (3), 22.2, 28.6 (3)"]
["","","","Type","","Brazing connection","Brazing connection","Brazing connection","Brazing connection","Brazing connection"]
["","Indoor unit","Gas","Type","","Brazing connection","Brazing connection","Brazing connection","Brazing connection","Brazing connection"]
["","","","OD","mm","9.5 (6), 12.7 (7), 15.9 (5)","9.5 (6), 12.7 (7), 15.9 (5)","9.5 (6), 12.7 (7), 15.9 (5)","9.5 (6), 12.7 (7), 15.9 (5)","9.5 (6), 12.7 (7), 15.9 (5)"]
["","","Liquid","OD","mm","6.4 (4), 9.5 (5)","6.4 (4), 9.5 (5)","6.4 (4), 9.5 (5)","6.4 (4), 9.5 (5)","6.4 (4), 9.5 (5)"]
["","","","Type","","Brazing connection","Brazing connection","Brazing connection","Brazing connection","Brazing connection"]
["BS units connected in Refrigerant Flow Through","Maximum total capacity index of indoor units","","","","750","750","750","750","750"]
["","Maximum total allowed amount of BS units","","","","4","4","4","4","4"]
["","Maximum total number of ports of BS units","","","","16","16","16","16","16"]
["Maximum capacity index of connectable indoor units per branch","","","","","140","140","140","140","140"]
["Sound power level","Nom.","","","dBA","49.1 (2)","51.5 (2)","51.5 (2)","52.5 (2)","52.5 (2)"]
["Dimensions","Unit","","Width","mm","600","1,000","1,000","1,400","1,400"]
["","","","Depth","mm","845","845","845","845","845"]
["","","","Height","mm","291","291","291","291","291"]
["Weight","Unit","","","kg","40.0","56.0","65.0","83.0","89.0"]
["Number of branches","","","","","4","6","8","10","12"]
["Maximum capacity index of connectable indoor units","","","","","400","600","750","750","750"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240","220-240"]
["Notes","","","","","(1) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(1) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(1) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(1) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(1) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(2) - Sound power level is an absolute value that a sound source generates.","(2) - Sound power level is an absolute value that a sound source generates.","(2) - Sound power level is an absolute value that a sound source generates.","(2) - Sound power level is an absolute value that a sound source generates.","(2) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(3) - Accessory pipe required","(3) - Accessory pipe required","(3) - Accessory pipe required","(3) - Accessory pipe required","(3) - Accessory pipe required"]
["","","","","","(4) - When connecting indoor units smaller or equal to 80 class (no need to cut the outlet pipe)","(4) - When connecting indoor units smaller or equal to 80 class (no need to cut the outlet pipe)","(4) - When connecting indoor units smaller or equal to 80 class (no need to cut the outlet pipe)","(4) - When connecting indoor units smaller or equal to 80 class (no need to cut the outlet pipe)","(4) - When connecting indoor units smaller or equal to 80 class (no need to cut the outlet pipe)"]
["","","","","","(5) - When connecting indoor units larger or equal to 100 class (the outlet pipe needs to be cut)","(5) - When connecting indoor units larger or equal to 100 class (the outlet pipe needs to be cut)","(5) - When connecting indoor units larger or equal to 100 class (the outlet pipe needs to be cut)","(5) - When connecting indoor units larger or equal to 100 class (the outlet pipe needs to be cut)","(5) - When connecting indoor units larger or equal to 100 class (the outlet pipe needs to be cut)"]
["","","","","","(6) - When connecting indoor units smaller or equal to 32 class (no need to cut the outlet pipe)","(6) - When connecting indoor units smaller or equal to 32 class (no need to cut the outlet pipe)","(6) - When connecting indoor units smaller or equal to 32 class (no need to cut the outlet pipe)","(6) - When connecting indoor units smaller or equal to 32 class (no need to cut the outlet pipe)","(6) - When connecting indoor units smaller or equal to 32 class (no need to cut the outlet pipe)"]
["","","","","","(7) - When connecting indoor units between 40 & 80 class (the outlet pipe needs to be cut)","(7) - When connecting indoor units between 40 & 80 class (the outlet pipe needs to be cut)","(7) - When connecting indoor units between 40 & 80 class (the outlet pipe needs to be cut)","(7) - When connecting indoor units between 40 & 80 class (the outlet pipe needs to be cut)","(7) - When connecting indoor units between 40 & 80 class (the outlet pipe needs to be cut)"]
["","","","","","(8) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(8) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(8) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(8) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(8) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(9) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(10) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker"]