{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":57,"n_cols":8,"rows_kept":57,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ERA-AYF"]
[]
[]
[]
[]
["","","","","","ERA200AMYFB","ERA250AMYFB","ERA300AMYFB"]
["Cooling capacity","Nom.","","35°CDB","kW","22.4 (1)","28","33.5 (1)"]
["Heating capacity","Nom.","","6°CWB","kW","22.4 (2)","28","33.5 (2)"]
["SEER","","","","","6.36 (3)","6.93 (3)","6.47 (3)"]
["SCOP","","","","","4.42 (3)","4.42 (3)","4.64 (3)"]
["Indoor index connection","Min.","","","","140","200","200"]
["","Max.","","","","200","250","300"]
["Dimensions","Unit","","Height","mm","1,430","1,615","1,615"]
["","","","Width","mm","940","940","940"]
["","","","Depth","mm","320","460","460"]
["Weight","Unit","","","kg","134","163","163"]
["Fan","External static pressure","","Max.","Pa","35","35","35"]
["Compressor","Type","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Operation range","Cooling","","Min.","°CDB","-5","-5","-5"]
["","","","Max.","°CDB","52","52","52"]
["","Heating","","Min.","°CWB","-20","-20","-20"]
["","","","Max.","°CWB","15.5","15.5","15.5"]
["Sound power level","Cooling","","Nom.","dBA","73.2 (4)","74","76.1 (4)"]
["Sound pressure level","Cooling","","Nom.","dBA","58.1 (5)","57","60"]
["Refrigerant","Type","","","","R-32","R-32","R-32"]
["","GWP","","","","675","675","675"]
["","Charge","","","tCO2Eq","3.51","4.73","4.79"]
["","Charge","","","kg","5.2","7","7.1"]
["Piping connections","Liquid","","Type","","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","9.52","9.52","12.7"]
["","Gas","","Type","","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","19.1","19.1","22.2"]
["","Total piping length","System","Actual","m","50 (6)","50 (6)","50 (6)"]
["Standard Accessories","Connection pipes","","","","1","2","1"]
["","Installation and operation manual","","","","1","1","1"]
["Power supply","Name","","","","Y1","Y1","Y1"]
["","Phase","","","","3N~","3N~","3N~"]
["","Frequency","","","Hz","50/60","50/60","50/60"]
["","Voltage","","","V","380-415/400","380-415/400","380-415/400"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - Defined for a system capacity ratio of 100% ± 5%, configured for complete air recirculation applications.","(3) - Defined for a system capacity ratio of 100% ± 5%, configured for complete air recirculation applications.","(3) - Defined for a system capacity ratio of 100% ± 5%, configured for complete air recirculation applications."]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(14) - Sound values are measured in a semi-anechoic room.","(14) - Sound values are measured in a semi-anechoic room.","(14) - Sound values are measured in a semi-anechoic room."]
["","","","","","(15) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(15) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(15) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(16) - Ssc: Short-circuit power","(16) - Ssc: Short-circuit power","(16) - Ssc: Short-circuit power"]
["","","","","","(17) - For detailed contents of standard accessories, see installation/operation manual","(17) - For detailed contents of standard accessories, see installation/operation manual","(17) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","","(18) - For AHU HEX volume limitations, refer to the engineering data book or installation manual","(18) - For AHU HEX volume limitations, refer to the engineering data book or installation manual","(18) - For AHU HEX volume limitations, refer to the engineering data book or installation manual"]