{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":57,"n_cols":8,"rows_kept":57,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","ERQ-AW1"]
[]
[]
[]
[]
["","","","","","ERQ125A7W1B","ERQ200A7W1B","ERQ250A7W1B"]
["Sound pressure level","Nom.","","","dBA","54","57","58"]
["Standard Accessories","Installation manual","","","","1","1","1"]
["","Operation manual","","","","1","1","1"]
["","Connection pipes","","","","4","4","4"]
["Refrigerant","Charge","","","TCO2Eq","12.9","16.1","17.5"]
["","GWP","","","","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","6.2","7.7","8.4"]
["","Type","","","","R-410A","R-410A","R-410A"]
["Operation range","Cooling","","Max.","°CDB","43","43","43"]
["","","","Min.","°CDB","-5","-5","-5"]
["","Heating","","Max.","°CWB","15","15","15"]
["","","","Min.","°CWB","-20","-20","-20"]
["Cooling capacity","Nom.","","","kW","14.0 (1)","22.4 (1)","28.0 (1)"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","9.52"]
["","","","Type","","Braze connection","Braze connection","Braze connection"]
["","Gas","","OD","mm","15.9","19.1","22.2"]
["","","","Type","","Braze connection","Braze connection","Braze connection"]
["Power input","Cooling","","Nom.","kW","3.52 (1)","5.22 (1)","7.42 (1)"]
["Sound power level","Nom.","","","dBA","72","78","78"]
["COP","","","","","4.00 (2)","4.50 (2)","4.09 (2)"]
["Dimensions","Unit","","Width","mm","635","930","930"]
["","","","Depth","mm","765","765","765"]
["","","","Height","mm","1,680","1,680","1,680"]
["Weight","Unit","","","kg","159","187","240"]
["Fan","Air flow rate","Heating","Nom.","m³/min","95","171","185"]
["","","Cooling","Nom.","m³/min","95","171","185"]
["EER","","","","","3.98 (1)","4.29 (1)","3.77 (1)"]
["Heating capacity","Nom.","","","kW","16.0 (2)","25.0 (2)","31.5 (2)"]
["Power supply","Phase","","","","3N~","3N~","3N~"]
["","Name","","","","W1","W1","W1"]
["","Frequency","","","Hz","50","50","50"]
["","Voltage","","","V","400","400","400"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19.0°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m"]
["","","","","","(3) - Sound values are measured in a semi-anechoic room.","(3) - Sound values are measured in a semi-anechoic room.","(3) - Sound values are measured in a semi-anechoic room."]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(6) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(6) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA"]
["","","","","","(10) - TOCA means the total value of each OC set.","(10) - TOCA means the total value of each OC set.","(10) - TOCA means the total value of each OC set."]
["","","","","","(11) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(11) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(11) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(12) - FLA means the full load amps of the fan motor.","(12) - FLA means the full load amps of the fan motor.","(12) - FLA means the full load amps of the fan motor."]
["","","","","","(13) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(13) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(13) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value."]
["","","","","","(14) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(14) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A","(14) - EN/IEC 61000-3-11: European/international technical standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated ≤ 75A"]
["","","","","","(15) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(15) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(15) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(16) - Short-circuit power","(16) - Short-circuit power","(16) - Short-circuit power"]
["","","","","","(17) - Contains fluorinated greenhouse gases","(17) - system impedance","(17) - system impedance"]
["","","","","","(18) - system impedance","(18) - Contains fluorinated greenhouse gases","(18) - Contains fluorinated greenhouse gases"]
["","","","","","(19) - MSC means the maximum current during start up of the compressor","(19) - MSC means the maximum current during start up of the compressor","(19) - MSC means the maximum current during start up of the compressor"]