{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":12,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWH-J-SS"]
[]
[]
[]
[]
["","","","","","EWWH090J-SS","EWWH110J-SS","EWWH120J-SS","EWWH130J-SS","EWWH150J-SS","EWWH180J-SS","EWWH200J-SS"]
["Sound pressure level","Cooling","","Nom.","dBA","79","79","79","79","79","79","79"]
["Operation range","Water side","Evaporator","Min.","°CDB","-5","-5","-5","-5","-5","-5","-5"]
["","","","Max.","°CDB","25","25","25","25","25","25","25"]
["Compressor","Type","","","","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor","Single screw compressor"]
["","Starting method","","","","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta"]
["","Quantity","","","","1","1","1","1","1","1","1"]
["Weight","Operation weight","","","kg","1,211","1,276","1,378","1,415","1,473","1,663","1,607"]
["","Unit","","","kg","1,177","1,233","1,334","1,366","1,416","1,600","1,675"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["Refrigerant","Type","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["","GWP","","","","7","7","7","7","7","7","7"]
["","Circuits","","Quantity","","1","1","1","1","1","1","1"]
["","Charge","","","kg","18","35","34","37","37","38","38"]
["Cooling capacity","Nom.","","","kW","88.77","107.1","115.1","133.5","150.1","181.6","200.6"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.6"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Power input","Cooling","","Nom.","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["Sound power level","Cooling","","Nom.","dBA","89","89","89","89","89","89","89"]
["Dimensions","Unit","","Width","mm","913","913","913","913","913","913","913"]
["","","","Depth","mm","2,684","2,684","2,684","2,684","2,684","2,684","2,684"]
["","","","Height","mm","1,020","1,020","1,020","1,020","1,020","1,020","1,020"]
["Capacity control","Minimum capacity","","","%","25","25","25","25","25","25","25"]
["","Method","","","","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless","Stepless"]
["Casing","Material","","","","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel"]
["","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["Water heat exchanger - evaporator","Type","","","","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger","Plate heat exchanger"]
["","Water pressure drop","Cooling","Nom.","kPa","10.7","10.9","19.3","19.3","17.8","16.8","20.1"]
["","Water volume","","","l","14","18","14","17","20","26","26"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Voltage range","","Max.","%","10","10","10","10","10","10","10"]
["","","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","Frequency","","","Hz","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400"]
["Unit","Max unit current for wires sizing","","","A","83","100","112","127","159","176","198"]
["","Starting current","","Max","A","153","153","197","197","197","290","290"]
["","Running current","Cooling","Nom.","A","39","44","55","60","65","76","84"]
["","","","Max","A","75","90","100","114","143","158","178"]
["Notes","","","","","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB","(1) - Cooling: EW 12°C; LW 7°C; ambient conditions: 35°CDB"]
["","","","","","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB","(2) - Cooling: EW 23°C; LW 18°C; ambient conditions: 35°CDB"]
["","","","","","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Condition: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Condition: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825","(5) - According to EN14825"]
["","","","","","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual.","(6) - Depends on operation mode, refer to installation manual."]
["","","","","","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing","(7) - For more details, see operation range drawing"]