{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":43,"n_cols":15,"rows_kept":43,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWH-VZSS"]
[]
[]
[]
[]
["","","","","EWWH445VZSSA1","EWWH515VZSSA1","EWWH550VZSSA1","EWWH660VZSSA1","EWWH770VZSSA1","EWWH860VZSSA2","EWWHC10VZSSA2","EWWHC12VZSSA2","EWWHC13VZSSA2","EWWHC14VZSSA2","EWWHC15VZSSA2"]
["Cooling capacity","Nom.","","kW","443","512","549","658","768","865","1,012","1,142","1,271","1,396","1,525"]
["Capacity control","Method","","","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable","Variable"]
["","Minimum capacity","","%","20","20","20","20","20","10","10","10","10","10","10"]
["Power input","Cooling","Nom.","kW","82.8","98.1","107","123","149","172","205","235","254","282","302"]
["EER","","","","5.35","5.22","5.15","5.34","5.14","5.02","4.93","4.87","5.01","4.95","5.04"]
["ESEER","","","","7.98","7.83","7.9","8.03","7.99","7.93","8.12","8","8.46","8","8.48"]
["Dimensions","Unit","Depth","mm","3,722","3,750","3,750","3,690","3,822","4,792","4,792","4,792","4,508","4,508","4,750"]
["","","Height","mm","2,123","2,123","2,123","2,292","2,487","2,296","2,296","2,296","2,350","2,338","2,498"]
["","","Width","mm","1,178","1,179","1,179","1,233","1,303","1,484","1,487","1,484","1,580","1,627","1,753"]
["Weight","Unit","","kg","2,892","2,928","2,941","3,451","4,237","5,570","5,820","6,220","6,890","7,260","8,260"]
["","Operation weight","","kg","2,977","3,033","3,053","3,611","4,488","5,980","6,290","6,690","7,480","7,830","9,070"]
["Water heat exchanger - evaporator","Type","","","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube","Flooded shell and tube"]
["","Water volume","","l","88","88","96","134","156","230","270","270","320","320","380"]
["Water heat exchanger - condenser","Type","","","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube","Shell and tube"]
["Compressor","Type","","","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor"]
["","Quantity","","","1","1","1","1","1","2","2","2","2","2","2"]
["Sound power level","Cooling","Nom.","dBA","101","105","105","105","107","106","107","107","108","108","110"]
["Sound pressure level","Cooling","Nom.","dBA","82","86","86","86","88","87","88","88","89","89","90"]
["Refrigerant","Charge","","kg","100","110","110","170","180","250","290","290","320","320","350"]
["","Circuits","Quantity","","1","1","1","1","1","2","2","2","2","2","2"]
["","GWP","","","7","7","7","7","7","7","7","7","7","7","7"]
["Refrigerant circuit","Charge","","kg","100","110","110","170","180","250","290","290","320","320","350"]
["Power supply","Phase","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Frequency","","Hz","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","V","400","400","400","400","400","400","400","400","400","400","400"]
["Notes","","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: evaporator 12.0/7.0°C; condenser 30/35.0°C, unit at full load operation, operating fluid: water, fouling factor = 0"]
["","","","","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744","(2) - Sound level data are measured at entering evaporator water temp. 12°C; leaving evaporator water temp. 7°C; entering condenser water temp. 30°C; leaving condenser water temp. 35°C; full load operation; standard: ISO3744"]
["","","","","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(3) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C","(4) - Nominal running current in cooling mode is referred to the following conditions: evaporator 12°C/7°C; condenser 30°C/35°C"]
["","","","","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope","(5) - Maximum running current is based on max compressor absorbed current in its envelope"]
["","","","","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(6) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1","(7) - Maximum current for wires sizing: compressor full load ampere x 1.1"]
["","","","","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options.","(8) - All data refers to the standard unit without options."]
["","","","","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data.","(9) - All data are subject to change without notice. Please refer to the unit nameplate data."]
["","","","","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS).","(10) - For more details on the operating limits please refer to the Chiller Selection Software (CSS)."]
["","","","","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels.","(11) - Equipment contains fluorinated greenhouse gases. Actual refrigerant charge depends on the final unit construction, details can be found on the unit labels."]
["","","","","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced.","(12) - In case of inverter driven units, no inrush current at start up is experienced."]