{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":51,"n_cols":12,"rows_kept":51,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXDQ-A3"]
[]
[]
[]
[]
["","","","","","FXDQ15A3VEB","FXDQ20A3VEB","FXDQ25A3VEB","FXDQ32A3VEB","FXDQ40A3VEB","FXDQ50A3VEB","FXDQ63A3VEB"]
["Sound pressure level","Cooling","","At low fan speed","dBA","27.0","27.0","27.0","27.0","28.0","29.0","30.0"]
["","","","At high fan speed","dBA","32.0","33.0","33.0","33.0","34.0","35.0","36.0"]
["","","","At medium fan speed","dBA","31.0","31.0","31.0","31.0","32.0","33.0","34.0"]
["Refrigerant","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.036 (1)","0.036 (1)","0.036 (1)","0.041 (1)","0.042 (1)","0.053 (1)","0.062 (1)"]
["","Heating","","At high fan speed","kW","0.036 (1)","0.036 (1)","0.036 (1)","0.041 (1)","0.042 (1)","0.053 (1)","0.062 (1)"]
["Cooling capacity","Nom.","","","kW","1.7","2.2","2.8","3.6","4.5","5.6","7.1"]
["Piping connections","Liquid","","OD","mm","6","6","6","6","6","6","10"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Gas","","OD","mm","12.7","12.7","12.7","12.7","12.7","12.7","15.9"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Drain","","","","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)"]
["Required ceiling void >","mm","","","","240","240","240","240","240","240","240"]
["Sound power level","Cooling","","At high fan speed","dBA","50","51","51","51","52","53","54"]
["Air filter","Type","","","","Removable / washable","Removable / washable","Removable / washable","Removable / washable","Removable / washable","Removable / washable","Removable / washable"]
["Dimensions","Unit","","Width","mm","750","750","750","750","950","950","1,150"]
["","","","Depth","mm","620","620","620","620","620","620","620"]
["","","","Height","mm","200","200","200","200","200","200","200"]
["Casing","Material","","","","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel","Galvanised steel"]
["","Colour","","","","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)"]
["Weight","Unit","","","kg","22","22","22","22","26","26","29"]
["Fan","External static pressure - 50Hz","","High","Pa","30.0","30.0","30.0","30.0","44.0","44.0","44.0"]
["","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","7.5","8.0","8.0","8.0","10.5","12.5","16.5"]
["","","","At low fan speed","m³/min","6.4","6.4","6.4","6.4","8.5","10.0","13.0"]
["Drain-up height","mm","","","","600","600","600","600","600","600","600"]
["Heating capacity","Nom.","","","kW","1.9","2.5","3.2","4.0","5.0","6.3","8.0"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","16","16","16","16","16","16","16"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~","1~"]
["","Name","","","","VE","VE","VE","VE","VE","VE","VE"]
["","Frequency","","","Hz","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting.","(1) - Values are valid for the factory setting."]
["","","","","","(2) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m","(2) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m","(2) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m","(2) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m","(2) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m","(2) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m","(2) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 5m; level difference: 0m"]
["","","","","","(3) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m","(3) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m","(3) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m","(3) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m","(3) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m","(3) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m","(3) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 5m; level difference: 0m"]
["","","","","","(4) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(4) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(4) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(4) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(4) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(4) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(4) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(5) - External static pressure is changeable to set by the remote control (from standard to high, see installation manual)","(5) - External static pressure is changeable to set by the remote control (from standard to high, see installation manual)","(5) - External static pressure is changeable to set by the remote control (from standard to high, see installation manual)","(5) - External static pressure is changeable to set by the remote control (from standard to high, see installation manual)","(5) - External static pressure is changeable to set by the remote control (from standard to high, see installation manual)","(5) - External static pressure is changeable to set by the remote control (from standard to high, see installation manual)","(5) - External static pressure is changeable to set by the remote control (from standard to high, see installation manual)"]
["","","","","","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA"]
["","","","","","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases","(10) - Contains fluorinated greenhouse gases"]
["","","","","","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker","(11) - Instead of a fuse, use a circuit breaker"]
["","","","","","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA","(12) - Select wire size based on the value of MCA"]
["","","","","","(13) - Next lower standard fuse rating minimum 15A","(13) - Next lower standard fuse rating minimum 15A","(13) - Next lower standard fuse rating minimum 15A","(13) - Next lower standard fuse rating minimum 15A","(13) - Next lower standard fuse rating minimum 15A","(13) - Next lower standard fuse rating minimum 15A","(13) - Next lower standard fuse rating minimum 15A"]