{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":65,"n_cols":13,"rows_kept":65,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXKQ-MA"]
[]
[]
[]
[]
["","","","","","FXKQ25MAVE9","FXKQ25MAVE","FXKQ32MAVE9","FXKQ32MAVE","FXKQ40MAVE9","FXKQ40MAVE","FXKQ63MAVE9","FXKQ63MAVE"]
["Sound pressure level","Cooling","","At low fan speed","dBA","33.0","33.0","33.0","33.0","34.0","34.0","37.0","37.0"]
["","","","At high fan speed","dBA","38.0","38.0","38.0","38.0","40.0","40.0","42.0","42.0"]
["Standard Accessories","Operation manual","","","","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual"]
["","Installation manual","","","","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual"]
["","Paper pattern for installation","","","","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation","Paper pattern for installation"]
["","Clamps","","","","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps"]
["","Insulation for hanger bracket","","","","Insulation for hanger bracket","Insulation for hanger bracket","Insulation for hanger bracket","Insulation for hanger bracket","Insulation for hanger bracket","Insulation for hanger bracket","Insulation for hanger bracket","Insulation for hanger bracket"]
["","Positioning jig for installation","","","","Positioning jig for installation","Positioning jig for installation","Positioning jig for installation","Positioning jig for installation","Positioning jig for installation","Positioning jig for installation","Positioning jig for installation","Positioning jig for installation"]
["","Drain hose","","","","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose"]
["","Clamp metal","","","","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal"]
["","Insulation for fitting","","","","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting"]
["","Sealing pads","","","","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads"]
["","Screws","","","","Screws","Screws","Screws","Screws","Screws","Screws","Screws","Screws"]
["","Washer","","","","Washer","Washer","Washer","Washer","Washer","Washer","Washer","Washer"]
["","Air outlet blocking pad","","","","Air outlet blocking pad","Air outlet blocking pad","Air outlet blocking pad","Air outlet blocking pad","Air outlet blocking pad","Air outlet blocking pad","Air outlet blocking pad","Air outlet blocking pad"]
["Refrigerant","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.066","0.066","0.066","0.066","0.076","0.076","0.105","0.105"]
["","Heating","","At high fan speed","kW","0.046","0.046","0.046","0.046","0.056","0.056","0.085","0.085"]
["Cooling capacity","Total capacity","","At high fan speed","kW","2.8 (1)","2.8 (1)","3.6 (1)","3.6 (1)","4.5 (1)","4.5 (1)","7.10 (1)","7.10 (1)"]
["Piping connections","Liquid","","OD","mm","6.4","6.35","6.4","6.35","6.4","6.35","9.5","9.52"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Gas","","OD","mm","12.7","12.7","12.7","12.7","12.7","12.7","15.9","15.9"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Drain","","","","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)"]
["Sound power level","Cooling","","At high fan speed","dBA","54","54","54","54","56","56","58","58"]
["Air filter","Type","","","","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance"]
["Dimensions","Unit","","Width","mm","1,110","1,110","1,110","1,110","1,110","1,110","1,310","1,310"]
["","","","Depth","mm","710","710","710","710","710","710","710","710"]
["","","","Height","mm","215","215","215","215","215","215","215","215"]
["Casing","Material","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["Weight","Unit","","","kg","31","31","31","31","31","31","34","34"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","11","11","11","11","13","13","18","18"]
["","","","At low fan speed","m³/min","9","9","9","9","10","10","15","15"]
["","Air flow rate - 60Hz","Cooling","High","m³/min","11","11","11","11","13","13","18","18"]
["","","","Low","m³/min","8.5","8.5","8.5","8.5","10","10","13","13"]
["Decoration panel","Weight","","","kg","8.5","8.5","8.5","8.5","8.5","8.5","9.5","9.5"]
["","Model","","","","BYK45FJW1","BYK45FJW1","BYK45FJW1","BYK45FJW1","BYK45FJW1","BYK45FJW1","BYK71FJW1","BYK71FJW1"]
["","Dimensions","","Height","mm","70","70","70","70","70","70","70","70"]
["","","","Depth","mm","800","800","800","800","800","800","800","800"]
["","","","Width","mm","1,240","1,240","1,240","1,240","1,240","1,240","1,440","1,440"]
["","Colour","","","","White","White","White","White","White","White","White","White"]
["Heating capacity","Total capacity","","At high fan speed","kW","3.2 (2)","3.2 (2)","4.0 (2)","4.0 (2)","5.0 (2)","5.0 (2)","8.00 (2)","8.00 (2)"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","15","15","15","15","15","15","15","15"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Name","","","","VE","VE","VE","VE","VE","VE","VE","VE"]
["","Frequency","","","Hz","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m (horizontal)"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m (horizontal)"]
["","","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(4) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%.","(5) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA","(6) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA","(7) - MFA ≤ 4 x FLA"]
["","","","","","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A","(8) - Next lower standard fuse rating minimum 15A"]
["","","","","","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA","(9) - Select wire size based on the value of MCA"]
["","","","","","(10) - Use a circuit breaker instead of a fuse.","(10) - Use a circuit breaker instead of a fuse.","(10) - Use a circuit breaker instead of a fuse.","(10) - Use a circuit breaker instead of a fuse.","(10) - Use a circuit breaker instead of a fuse.","(10) - Use a circuit breaker instead of a fuse.","(10) - Use a circuit breaker instead of a fuse.","(10) - Use a circuit breaker instead of a fuse."]
["","","","","","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases","(11) - Contains fluorinated greenhouse gases"]