{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":61,"n_cols":9,"rows_kept":61,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXUQ-A"]
[]
[]
[]
[]
["","","","","","FXUQ71AVEB","FXUQ71AVEB9","FXUQ100AVEB","FXUQ100AVEB9"]
["Sound pressure level","Heating","","At high fan speed","dBA","40.0","40.0","47.0","47.0"]
["","","","At low fan speed","dBA","36.0","36.0","40.0","40.0"]
["","","","At medium fan speed","dBA","38.0","38.0","44.0","44.0"]
["","Cooling","","At low fan speed","dBA","36.0","36.0","40.0","40.0"]
["","","","At high fan speed","dBA","40.0","40.0","47.0","47.0"]
["","","","At medium fan speed","dBA","38.0","38.0","44.0","44.0"]
["Standard Accessories","Operation manual","","","","Operation manual","Operation manual","Operation manual","Operation manual"]
["","Installation manual","","","","Installation manual","Installation manual","Installation manual","Installation manual"]
["","Declaration of conformity","","","","Declaration of conformity","Declaration of conformity","Declaration of conformity","Declaration of conformity"]
["","Drain hose","","","","Drain hose","Drain hose","Drain hose","Drain hose"]
["","Clamp metal","","","","Clamp metal","Clamp metal","Clamp metal","Clamp metal"]
["","Washer for hanger bracket","","","","Washer for hanger bracket","Washer for hanger bracket","Washer for hanger bracket","Washer for hanger bracket"]
["","Clamps","","","","Clamps","Clamps","Clamps","Clamps"]
["","Washer clamp","","","","Washer clamp","Washer clamp","Washer clamp","Washer clamp"]
["","Joint insulating material","","","","Joint insulating material","Joint insulating material","Joint insulating material","Joint insulating material"]
["","Sealing material","","","","Sealing material","Sealing material","Sealing material","Sealing material"]
["","Elbow","","","","Elbow","Elbow","Elbow","Elbow"]
["","Installation pattern","","","","Installation pattern","Installation pattern","Installation pattern","Installation pattern"]
["","Blocking material","","","","Blocking material","Blocking material","Blocking material","Blocking material"]
["","L-bent piping","","","","L-bent piping","L-bent piping","L-bent piping","L-bent piping"]
["","Screws","","","","Screws","Screws","Screws","Screws"]
["","Non woven fabric","","","","Non woven fabric","Non woven fabric","Non woven fabric","Non woven fabric"]
["Refrigerant","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","0.090","0.090","0.200","0.200"]
["","Heating","","At high fan speed","kW","0.073","0.073","0.179","0.179"]
["Cooling capacity","Total capacity","","At high fan speed","kW","8.0","8.0","11.2","11.2"]
["Piping connections","Liquid","","OD","mm","9.52","9.5","9.52","9.5"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Gas","","OD","mm","15.9","15.9","15.9","15.9"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Drain","","","","I.D. 20/O.D. 26","I.D. 20/O.D. 26","I.D. 20/O.D. 26","I.D. 20/O.D. 26"]
["Sound power level","Cooling","","At high fan speed","dBA","58","58","65","65"]
["Air filter","Type","","","","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance","Resin net with mold resistance"]
["Dimensions","Unit","","Width","mm","950","950","950","950"]
["","","","Depth","mm","950","950","950","950"]
["","","","Height","mm","198","198","198","198"]
["Casing","Material","","","","Resin","Resin","Resin","Resin"]
["","Colour","","","","Fresh White","Fresh White","Fresh White","Fresh White"]
["Weight","Unit","","","kg","26","26","27","27"]
["Fan","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","22.5","22.5","31.0","31.0"]
["","","","At low fan speed","m³/min","16.0","16.0","21.0","21.0"]
["Heating capacity","Total capacity","","At high fan speed","kW","9.0","9.0","12.5","12.5"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","16","16","16","16"]
["Power supply","Phase","","","","1~","1~","1~","1~"]
["","Frequency","","","Hz","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220-230","220-240/220-230","220-240/220-230","220-240/220-230"]
["Notes","","","","","(1) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(1) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(1) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(1) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(2) - Maximum allowable voltage range variation between phases is 2%.","(2) - Maximum allowable voltage range variation between phases is 2%.","(2) - Maximum allowable voltage range variation between phases is 2%.","(2) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(3) - MCA/MFA: MCA = 1.25 x FLA","(3) - MCA/MFA: MCA = 1.25 x FLA","(3) - MCA/MFA: MCA = 1.25 x FLA","(3) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(4) - MFA ≤ 4 x FLA","(4) - MFA ≤ 4 x FLA","(4) - MFA ≤ 4 x FLA","(4) - MFA ≤ 4 x FLA"]
["","","","","","(5) - Next lower standard fuse rating minimum 16A","(5) - Next lower standard fuse rating minimum 16A","(5) - Next lower standard fuse rating minimum 16A","(5) - Next lower standard fuse rating minimum 16A"]
["","","","","","(6) - Select wire size based on the value of MCA","(6) - Select wire size based on the value of MCA","(6) - Select wire size based on the value of MCA","(6) - Select wire size based on the value of MCA"]
["","","","","","(7) - Instead of a fuse, use a circuit breaker","(7) - Instead of a fuse, use a circuit breaker","(7) - Instead of a fuse, use a circuit breaker","(7) - Instead of a fuse, use a circuit breaker"]
["","","","","","(8) - Contains fluorinated greenhouse gases","(8) - Contains fluorinated greenhouse gases","(8) - Contains fluorinated greenhouse gases","(8) - Contains fluorinated greenhouse gases"]