{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":99,"n_cols":8,"rows_kept":99,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","SB.RKXYQ-T"]
[]
[]
[]
[]
["","","","","","SB.RKXYQ8T7Y1B","SB.RKXYQ8T","SB.RKXYQ5T (Archived)"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - Actual number of units depends on the indoor unit type (VRV DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤ 130%).","(3) - Actual number of units depends on the indoor unit type (VRV DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤ 130%).","(3) - Actual number of units depends on the indoor unit type (VRV DX indoor, etc.) and the connection ratio restriction for the system (being; 50% ≤ CR ≤ 130%)."]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set."]
["","","","","","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan"]
["","","","","","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room."]
["","","","","","(17) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(17) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(17) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(18) - Ssc: Short-circuit power","(18) - Ssc: Short-circuit power","(18) - Ssc: Short-circuit power"]
["","","","","","(19) - For detailed contents of standard accessories, see installation/operation manual","(19) - For detailed contents of standard accessories, see installation/operation manual","(19) - For detailed contents of standard accessories, see installation/operation manual"]
["SEER recommended combination 2","","","","","","4.8"]
["Capacity range","HP","","","","","8","5"]
["Operation range","Cooling","","Max.","°CDB","","46.0","46.0"]
["","","","Min.","°CDB","","-5.0","-5.0"]
["","Heating","","Min.","°CWB","","-20.0","-20.0"]
["","","","Max.","°CWB","","15.5","15.5"]
["ηs,c","%","","","","","191.1"]
["Maximum number of connectable indoor units","","","","","","17 (3)","10 (3)"]
["Space cooling","B Condition (30°C - 27/19)","","Pdc","kW","","16.5","10.3"]
["","","","EERd","","","3.7","4.0"]
["","D Condition (20°C - 27/19)","","Pdc","kW","","6.4","4.8"]
["","","","EERd","","","10.5","9.4"]
["","A Condition (35°C - 27/19)","","EERd","","","2.2","2.4"]
["","","","Pdc","kW","","22.4","14.0"]
["","C Condition (25°C - 27/19)","","EERd","","","5.5","6.5"]
["","","","Pdc","kW","","10.6","6.6"]
["SCOP","","","","","","3.6","3.8"]
["Refrigerant","GWP","","","","","2,087.5"]
["Space cooling recommended combination 2","C Condition (25°C - 27/19)","","Pdc","kW","","10.6"]
["","","","EERd","","","5.6"]
["","A Condition (35°C - 27/19)","","EERd","","","2.1"]
["","","","Pdc","kW","","22.4"]
["","D Condition (20°C - 27/19)","","EERd","","","10.7"]
["","","","Pdc","kW","","6.4"]
["","B Condition (30°C - 27/19)","","EERd","","","3.7"]
["","","","Pdc","kW","","16.5"]
["System","Compressor unit","","","","","RKXYQ8T","RKXYQ5T"]
["","Heat exchanger unit","","","","","RDXYQ8T","RDXYQ5T"]
["Recommended combination 2","","","","","","4 x FXSQ50A2VEB"]
["SCOP recommended combination 2","","","","","","3.5"]
["Power input - 50Hz","Heating","Nom.","6°CWB","kW","","6.8 (2)","3.5 (2)"]
["Indoor index connection","Min.","","","","","100.0","62.5"]
["","Max.","","","","","260.0","162.5"]
["Cooling capacity","Prated,c","","","kW","","22.4 (1)"]
["COP at nom. capacity","6°CWB","","","kW/kW","","3.3","4.0"]
["Recommended combination","","","","","","4 x FXMQ50P7VEB","4 x FXSQ32A2VEB"]
["Space heating (Average climate)","TOL","","COPd (declared COP)","","","2.0","2.2"]
["","","","Pdh (declared heating cap)","kW","","12.9","10.4"]
["","","","Tol (temperature operating limit)","°C","","-10.0","-10.0"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","","6.0","4.1"]
["","","","COPd (declared COP)","","","7.3","5.2"]
["","B Condition (2°C)","","COPd (declared COP)","","","3.0","3.3"]
["","","","Pdh (declared heating cap)","kW","","6.9","5.6"]
["","C Condition (7°C)","","COPd (declared COP)","","","6.6","7.1"]
["","","","Pdh (declared heating cap)","kW","","5.4","3.6"]
["","A Condition (-7°C)","","COPd (declared COP)","","","2.3","2.4"]
["","","","Pdh (declared heating cap)","kW","","11.4","9.2"]
["","TBivalent","","Pdh (declared heating cap)","kW","","12.9","10.4"]
["","","","Tbiv (bivalent temperature)","°C","","-10.0","-10.0"]
["","","","COPd (declared COP)","","","2.0","2.2"]
["Piping connections","Between Compressor module (CM) and indoor units (IU)","Liquid","OD","mm","","9.52","9.52"]
["","","Gas","OD","mm","","19.1","15.9"]
["","Total piping length","System","Actual","m","","300 (6)","140 (6)"]
["","Between Compressor module (CM) and heat exchanger module (HM)","Gas","OD","mm","","22.2","19.1"]
["","","Liquid","OD","mm","","12.7","12.7"]
["","","Piping length","Max.","m","","30.0","30.0"]
["SEER","","","","","","4.9","5.1"]
["Space heating (Average climate) recommended combination 2","B Condition (2°C)","","Pdh (declared heating cap)","kW","","6.9"]
["","","","COPd (declared COP)","","","3.0"]
["","C Condition (7°C)","","Pdh (declared heating cap)","kW","","4.9"]
["","","","COPd (declared COP)","","","5.9"]
["","A Condition (-7°C)","","COPd (declared COP)","","","2.3"]
["","","","Pdh (declared heating cap)","kW","","11.4"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","","6.0"]
["","","","COPd (declared COP)","","","7.2"]
["","TBivalent","","Pdh (declared heating cap)","kW","","12.9"]
["","","","COPd (declared COP)","","","2.0"]
["","","","Tbiv (bivalent temperature)","°C","","-10.0"]
["Sound power level","Cooling","","Nom.","dBA","","81.0 (4)"]
["ηs,h","%","","","","","140.9"]
["Fan","External static pressure","","Max.","Pa","","150","150"]
["Heating capacity","Prated,h","","","kW","","12.9"]
["","Nom.","","6°CWB","kW","","22.4 (2)","14.0 (2)"]