{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":64,"n_cols":12,"rows_kept":64,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","VAM-J"]
[]
[]
[]
[]
["","","","","","VAM350J7VEB","VAM500J7VEB","VAM650J7VEB","VAM800J7VEB","VAM1000J7VEB","VAM1500J7VEB","VAM2000J7VEB"]
["Operation range","Min.","","","°CDB","","-10 (2)","-10 (2)","-10 (2)","-10 (2)","-10 (2)","-10 (2)"]
["","Max.","","","°CDB","","46","46","46","46","46","46"]
["","Around unit","","","°CDB","","0°C~40°CDB, 80% RH or less","0°C~40°CDB, 80% RH or less","0°C~40°CDB, 80% RH or less","0°C~40°CDB, 80% RH or less","0°C~40°CDB, 80% RH or less","0°C~40°CDB, 80% RH or less"]
["","Relative humidity","","","%","","80 or less","80 or less","80 or less","80 or less","80 or less","80 or less"]
["Weight","Unit","","","kg","","46.5","61.5","76.5","76.5","160","160"]
["Heat exchange system","","","","","","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange","Air to air cross flow total heat (sensible + latent heat) exchange"]
["Operation mode","","","","","","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode","Heat exchange mode, bypass mode, fresh-up mode"]
["Sound power level (Lwa)","dB","","","","51","54","58","58","61","62","65"]
["Power input - 50Hz","Heat exchange mode","Nom.","Ultra high","kW","","0.164 (1)","0.247 (1)","0.303 (1)","0.416 (1)","0.548 (1)","0.833 (1)"]
["","Bypass mode","Nom.","Ultra high","kW","","0.148 (1)","0.195 (1)","0.289 (1)","0.417 (1)","0.525 (1)","0.835 (1)"]
["Heat exchange element","","","","","","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper","Specially processed non-flammable paper"]
["Sound pressure level - 50Hz","Heat exchange mode","","Ultra high","dBA","","37.5 (1)","","39.0 (1)","42.0 (1)","42.0 (1)","45.0 (1)"]
["","Bypass mode","","Ultra high","dBA","","38.0 (1)","","40.0 (1)","42.5 (1)","42.0 (1)","45.0 (1)"]
["Dimensions","Unit","","Width","mm","","1,113","1,354","1,354","1,354","1,354","1,354"]
["","","","Depth","mm","","866","920","1,172","1,172","1,172","1,172"]
["","","","Height","mm","","305","368","368","368","731","731"]
["Casing","Material","","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["Fan","External static pressure - 50Hz","","Ultra high","Pa","","90.0 (1)","90.0 (1)","90.0 (1)","90.0 (1)","90.0 (1)","90.0 (1)"]
["","Air flow rate - 50Hz","Heat exchange mode","Ultra high","m³/h","","500 (1)","650 (1)","800 (1)","1,000 (1)","1,500 (1)","2,000 (1)"]
["","","Bypass mode","Ultra high","m³/h","","500 (1)","650 (1)","800 (1)","1,000 (1)","1,500 (1)","2,000 (1)"]
["Connection duct diameter","mm","","","","","200","250","250","250","2x250","2x250"]
["Power supply","Phase","","","","","1~","1~","1~","1~","1~","1~"]
["","Name","","","","","VE","VE","VE","VE","VE","VE"]
["","Frequency","","","Hz","","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","(1) - Measured according to JIS B 8628 - 2003","(1) - Measured according to JIS B 8628 - 2003","(1) - Measured according to JIS B 8628 - 2003","(1) - Measured according to JIS B 8628 - 2003","(1) - Measured according to JIS B 8628 - 2003","(1) - Measured according to JIS B 8628 - 2003","(1) - Measured according to JIS B 8628 - 2003"]
["","","","","","(2) - When the heat reclaim ventilation unit is installed upside down, the minimal allowed outdoor air temperature is 5°C.","(2) - When the heat reclaim ventilation unit is installed upside down, the minimal allowed outdoor air temperature is 5°C.","(2) - When the heat reclaim ventilation unit is installed upside down, the minimal allowed outdoor air temperature is 5°C.","(2) - When the heat reclaim ventilation unit is installed upside down, the minimal allowed outdoor air temperature is 5°C.","(2) - When the heat reclaim ventilation unit is installed upside down, the minimal allowed outdoor air temperature is 5°C.","(2) - When the heat reclaim ventilation unit is installed upside down, the minimal allowed outdoor air temperature is 5°C.","(2) - When the heat reclaim ventilation unit is installed upside down, the minimal allowed outdoor air temperature is 5°C."]
["","","","","","(3) - In accordance with commission regulation (EU) No 1253/2014","(3) - In accordance with commission regulation (EU) No 1253/2014","(3) - In accordance with commission regulation (EU) No 1253/2014","(3) - In accordance with commission regulation (EU) No 1253/2014","(3) - In accordance with commission regulation (EU) No 1253/2014","(3) - In accordance with commission regulation (EU) No 1253/2014","(3) - In accordance with commission regulation (EU) No 1253/2014"]
["","","","","","(4) - Measured according to EN308 : 1997","(4) - Measured according to EN308 : 1997","(4) - Measured according to EN308 : 1997","(4) - Measured according to EN308 : 1997","(4) - Measured according to EN308 : 1997","(4) - Measured according to EN308 : 1997","(4) - Measured according to EN308 : 1997"]
["","","","","","(5) - In accordance with regulation (EU) No 327/2011","(5) - Clean the filter when the filter icon appears on the controller screen. Regular filter cleaning is important for delivered air quality and for the unit's energy efficiency.","(5) - Clean the filter when the filter icon appears on the controller screen. Regular filter cleaning is important for delivered air quality and for the unit's energy efficiency.","(5) - Clean the filter when the filter icon appears on the controller screen. Regular filter cleaning is important for delivered air quality and for the unit's energy efficiency.","(5) - Clean the filter when the filter icon appears on the controller screen. Regular filter cleaning is important for delivered air quality and for the unit's energy efficiency.","(5) - Clean the filter when the filter icon appears on the controller screen. Regular filter cleaning is important for delivered air quality and for the unit's energy efficiency.","(5) - Clean the filter when the filter icon appears on the controller screen. Regular filter cleaning is important for delivered air quality and for the unit's energy efficiency."]
["","","","","","","(6) - In accordance with regulation (EU) No 327/2011","(6) - In accordance with regulation (EU) No 327/2011","(6) - In accordance with regulation (EU) No 327/2011","(6) - In accordance with regulation (EU) No 327/2011","(6) - In accordance with regulation (EU) No 327/2011","(6) - In accordance with regulation (EU) No 327/2011"]
["","","","","","","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","","(8) - MCA= 1,25x(FLA(FM1)+FLA(FM2)+FLA(FM3)+FLA(FM4))","(8) - MCA= 1,25x(FLA(FM1)+FLA(FM2)+FLA(FM3)+FLA(FM4))","(8) - MCA= 1,25x(FLA(FM1)+FLA(FM2)+FLA(FM3)+FLA(FM4))","(8) - MCA= 1,25x(FLA(FM1)+FLA(FM2)+FLA(FM3)+FLA(FM4))","(8) - MCA= 1,25x(FLA(FM1)+FLA(FM2)+FLA(FM3)+FLA(FM4))","(8) - MCA= 1,25x(FLA(FM1)+FLA(FM2)+FLA(FM3)+FLA(FM4))"]
["","","","","","","(9) - MCA represents maximum input current.","(9) - MCA represents maximum input current.","(9) - MCA represents maximum input current.","(9) - MCA represents maximum input current.","(9) - MCA represents maximum input current.","(9) - MCA represents maximum input current."]
["","","","","","","(10) - MFA ≤ 4 x (FLA(FM1)+FLA(FM2)+...)","(10) - MFA ≤ 4 x (FLA(FM1)+FLA(FM2)+...)","(10) - MFA ≤ 4 x (FLA(FM1)+FLA(FM2)+...)","(10) - MFA ≤ 4 x (FLA(FM1)+FLA(FM2)+...)","(10) - MFA ≤ 4 x (FLA(FM1)+FLA(FM2)+...)","(10) - MFA ≤ 4 x (FLA(FM1)+FLA(FM2)+...)"]
["","","","","","","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA"]
["","","","","","","(12) - Fan step 8 is nominal specs.","(12) - Fan step 8 is nominal specs.","(12) - Fan step 8 is nominal specs.","(12) - Fan step 8 is nominal specs.","(12) - Fan step 8 is nominal specs.","(12) - Fan step 8 is nominal specs."]
["","","","","","","(13) - The unit complies for \"Code du travail\" and \"ERP 5e catégorie\" applications according to French legislation.","(13) - The unit complies for \"Code du travail\" and \"ERP 5e catégorie\" applications according to French legislation.","(13) - The unit complies for \"Code du travail\" and \"ERP 5e catégorie\" applications according to French legislation.","(13) - The unit complies for \"Code du travail\" and \"ERP 5e catégorie\" applications according to French legislation.","(13) - The unit complies for \"Code du travail\" and \"ERP 5e catégorie\" applications according to French legislation.","(13) - The unit complies for \"Code du travail\" and \"ERP 5e catégorie\" applications according to French legislation."]
["","","","","","","(14) - \"Code du travail\" applications are non-public buildings (example offices).","(14) - \"Code du travail\" applications are non-public buildings (example offices).","(14) - \"Code du travail\" applications are non-public buildings (example offices).","(14) - \"Code du travail\" applications are non-public buildings (example offices).","(14) - \"Code du travail\" applications are non-public buildings (example offices).","(14) - \"Code du travail\" applications are non-public buildings (example offices)."]
["","","","","","","(15) - \"ERP (Etablissement Recevant du Public) de 5e catégorie\" are smaller shops, hotels etc","(15) - \"ERP (Etablissement Recevant du Public) de 5e catégorie\" are smaller shops, hotels etc","(15) - \"ERP (Etablissement Recevant du Public) de 5e catégorie\" are smaller shops, hotels etc","(15) - \"ERP (Etablissement Recevant du Public) de 5e catégorie\" are smaller shops, hotels etc","(15) - \"ERP (Etablissement Recevant du Public) de 5e catégorie\" are smaller shops, hotels etc","(15) - \"ERP (Etablissement Recevant du Public) de 5e catégorie\" are smaller shops, hotels etc"]
["Power input - 50Hz","Heat exchange mode","Nom.","Ultra high","kW","0.097 (1)"]
["","Bypass mode","Nom.","Ultra high","kW","0.085 (1)"]
["Dimensions","Unit","","Height","mm","305"]
["","","","Width","mm","1113"]
["","","","Depth","mm","866"]
["Weight","Unit","","","kg","46.5"]
["Fan","Air flow rate - 50Hz","Heat exchange mode","Ultra high","m³/h","350 (1)"]
["","","Bypass mode","Ultra high","m³/h","350 (1)"]
["","External static pressure - 50Hz","","Ultra high","Pa","90.0 (1)"]
["Operation range","Min.","","","°CDB","-10 (2)"]
["","Max.","","","°CDB","46"]
["Sound pressure level - 50Hz","Heat exchange mode","","Ultra high","dBA","34.5 (1)"]
["","Bypass mode","","Ultra high","dBA","34.5 (1)"]
["Power supply","Phase","","","","1~"]
["","Frequency","","","Hz","50/60"]
["","Voltage","","","V","220-240/220"]
["Sound pressure level - 50Hz","Heat exchange mode","","Ultra high","dBA","","","39.0 (1)"]
["","Bypass mode","","Ultra high","dBA","","","38.0 (1)"]