{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":20,"n_cols":9,"rows_kept":20,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","VH-B"]
[]
[]
[]
[]
["","","","VH1B","VH2B","VH3B","VH4/AB","VH4B","VH5B"]
["Output current (maximum)","","","19A at 40°C (ambient)","19A at 40°C (ambient)","19A at 40°C (ambient)","19A at 40°C (ambient)","19A at 40°C (ambient)","19A at 40°C (ambient)"]
["Connectable unit","","","VAM150FA","VAM250FA, VAM350FB","VAM500FB, VAM650FB","VAM800FB, VAM1000FB","VAM800FB, VAM1000FB","VAM1500FB, VAM2000FB"]
["LED indicators","","","Power ON - Yellow, Heater ON - Red (solid or flashing, indicating pulsed control), Airflow fault - Red","Power ON - Yellow, Heater ON - Red (solid or flashing, indicating pulsed control), Airflow fault - Red","Power ON - Yellow, Heater ON - Red (solid or flashing, indicating pulsed control), Airflow fault - Red","Power ON - Yellow, Heater ON - Red (solid or flashing, indicating pulsed control), Airflow fault - Red","Power ON - Yellow, Heater ON - Red (solid or flashing, indicating pulsed control), Airflow fault - Red","Power ON - Yellow, Heater ON - Red (solid or flashing, indicating pulsed control), Airflow fault - Red"]
["Run relay","","","1A 120V AC or 1A 24V DC","1A 120V AC or 1A 24V DC","1A 120V AC or 1A 24V DC","1A 120V AC or 1A 24V DC","1A 120V AC or 1A 24V DC","1A 120V AC or 1A 24V DC"]
["Duct diameter","mm","","100","150","200","250","250","350"]
["Capacity","kW","","1.0","1.0","1.0","2.5","1.5","2.5"]
["Mounting holes","","","98mm x 181mm centres 5mm Ø holes","98mm x 181mm centres 5mm Ø holes","98mm x 181mm centres 5mm Ø holes","98mm x 181mm centres 5mm Ø holes","98mm x 181mm centres 5mm Ø holes","98mm x 181mm centres 5mm Ø holes"]
["Maximum ambient adjacent to terminal box","","","35°C (during operation)","35°C (during operation)","35°C (during operation)","35°C (during operation)","35°C (during operation)","35°C (during operation)"]
["Temperature sensor","","","5k ohms at 25°C (table 502 1T)","5k ohms at 25°C (table 502 1T)","5k ohms at 25°C (table 502 1T)","5k ohms at 25°C (table 502 1T)","5k ohms at 25°C (table 502 1T)","5k ohms at 25°C (table 502 1T)"]
["BMS setpoint input","","","0-10VDC","0-10VDC","0-10VDC","0-10VDC","0-10VDC","0-10VDC"]
["Temperature control range","","","0 to 40°C / (0-10V 0-100%)","0 to 40°C / (0-10V 0-100%)","0 to 40°C / (0-10V 0-100%)","0 to 40°C / (0-10V 0-100%)","0 to 40°C / (0-10V 0-100%)","0 to 40°C / (0-10V 0-100%)"]
["Control fuse","","","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA","20 x 5mm 250 mA"]
["Power supply","Frequency","Hz","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","V","220/250","220/250","220/250","220/250","220/250","220/250"]